From:  		Fax:

Email:

Request for QUOTATION from AMERACE

For a Waterproof Voltage Transformer

Fax +1 905 882 8014

Transformer Technology

All transformers use the same technology, as listed under "Common Specifications" below.

In addition, you may choose any of the following options. Please be sure to complete each section.

Power Rating

30W	 45W	 65W	 100W	 150W

200W	 250W	 300W	 400W	 500W	Other ______W (max.600W)

Primary lead length

0,6 meter	 Other _________ meters (minimum 0,3, maximum ?)

Primary Connectors

First lead	  T Connector	 FAA Style 2 plug	 FAA Style 9 receptacle	 None

Second lead	  T Connector	 FAA Style 2 plug	 FAA Style 9 receptacle	 None

Secondary lead length

1,2 meters	 Other _________ meters (minimum 0,3, maximum ?)

Secondary Connectors

FAA Style 7		 FAA Style 8  	 None

Primary Voltage

110V	 220V	 360V	 480V	 600V	 2400V	 Other _____A

(max.4500V)

Secondary Voltage

6,9V	 12V	 15V	 30V	 45V	 110V	 220V	 Other _____A

(max.600V)

Common Specifications

Construction

Core	Flat laminations (E&I) of high grade grain oriented silicon steel for a long, stable life.

Encapsulant	TPR rubber (also known as TPV, TPE)

•	Much higher dielectric strength and lower water absorption than older materials such as epoxy, neoprene, or polychloroprene.

•	Minimal swelling in the presence of hydrocarbons, unlike neoprene, polychloroprene, etc.

Encapsulation process	Injection molding for maximum consistency of encapsulation, yielding exceptionally low leakage currents. Vacuum drawing prior to injection prevents air pockets inside. A far superior process to compression or transfer molding, or pouring.

Winding	Magnet wire on a plastic bobbin, specifically designed to electrically isolate the primary and secondary windings for maximum safety.

Connector pins and sockets	Tin plated for corrosion resistance

Primary cables	Cable is AWG #8 (8,3 mm2) Type C TPR for maximum reliability

Secondary cable	Cable is AWG 2/12 (3,3 mm2)

Material compatibility	Transformer body, cables, and connectors are all molded of TPR for perfect bonding.

Waterproofness	Amerace® transformers are designed and manufactured to operate submerged in water indefinitely.

Electrical

Insulation Level	5000 V RMS

Efficiencies	85% to 95% depending on the power rating

Power Factor 	> 0,97 for resistive leads

Frequency	50/60 Hz

Certification	Responsibility of buyer to obtain approval for use from local electrical authority

Testing	All units (100%) are hipotted and the output voltage confirmed

Environmental

Operating Temperature Range	-55°C to +65°C

Contaminant resistance	Suitable for areas contaminated with most oils, aircraft fuels, soil acids and alkalis, and deicing fluids. Resistant to UV exposure and ozone.

Installation Options	All types, including above ground, in concrete or other non-metallic pits, in metal cans, or direct buried.

Voltage Spec.